## Instructions
Process for calculating rainwater flowing off a roof:
1. Figure out square footage of the building on each side of the roof (Length * Width of the barn from peak to side including any sheds present, picture below )
2. How many downspouts are on each side?
3. What is an expected 1 hour rainfall event for your location?
a. For 1 hour (60 minute) rainfall totals:
NOAA web tool: https://hdsc.nws.noaa.gov/hdsc/pfds/pfds_map_cont.html?bkmrk=ky
4. Allow excel sheet to calculate rainfall totals. The publication linked below should output useful data for sizing gutters and downspouts:
a. Plumbing code Particularly Table 1106.2
| Width 1 | Width 2

## Rainfall Calculations
Adjust Values In Red
Roof 1 Area | 2000 | ft 2
Roof 2 Area | 2500 | ft 2
Downspouts (side 1) | 2 | #
Downspouts (side 2) | 2 | #
5 Year-60 Min Rainfall Event | 1.73 | inch
10 Year-60 Min Rainfall Event | 1.99 | inch
25 Year-60 Min Rainfall Event | 2.32 | inch
Cubic Feet of Rainfall in 1 Hour Storm | Frequency of Storm Event
| 5 Year | 10 Year | 25 Year
Roof 1 | 288.3333 | 331.6667 | 386.6667
Roof 2 | 360.4167 | 414.5833 | 483.3333
Gallons per Minute of Total Rainfall onto Roof | Frequency of Storm Event
| 5 Year | 10 Year | 25 Year
Roof 1 | 35.9456 | 41.3478 | 48.2044
Roof 2 | 44.9319 | 51.6847 | 60.2556
Gallon Per Minute through Each Downspout | Frequency of Storm Event
(assumes water is evenly divided) | 5 Year | 10 Year | 25 Year
Roof 1 | 17.9728 | 20.6739 | 24.1022
Roof 2 | 22.466 | 25.8424 | 30.1278